SAIA - P8  REDUCED PROTOCOL DESCRIPTION                       Page: 1

SAIA - P8 REDUCED PROTOCOL DESCRIPTION

+======================================+

REVISION HISTORY        DD-EPFW6-024

+------------------------------------+

23/11/93  GK  Creation based on full description

3/1/93    GK  Corrected layout of document

1. INTRODUCTION

------------

1.1. Purpose

-------

The purpose of this document is the specification of the datagrams and

functions used in the SAIA-P8  protocol and its relation to the

transmission protocols.

1.2. Scope

-----

The SAIA-P8  Protocol allows the exchange of medias and the program

control between different PCD stations and between PCD station and

Programming Units and/or Process Management Systems.  The SAIA-P8

Protocol may be used over any byte transparent connection (asynchronous

connections or OSI Transport Protocols).

The scope of the document is the definition of the syntax and procedures

of the application, presentation and session layer protocols.

SAIA - P8  REDUCED PROTOCOL DESCRIPTION                       Page: 2

TABLE OF CONTENTS

=================

1. INTRODUCTION ......................................................1

1.1. Purpose .........................................................1

1.2. Scope ...........................................................1

1.3. Definitions and Abbreviations ...................................3

1.4. References ......................................................3

2. GENERAL DESCRIPTION ...............................................4

3. APPLICATION LAYER .................................................4

3.1. Modelling the provided Service ..................................4

3.2. Formats of the Medias ...........................................4

3.2.1. Binary Format .................................................4

3.2.2. Integer Format ................................................4

3.2.3. Floating-Point Format .........................................5

3.3. Application Service .............................................6

3.3.1. Variable Access Service .......................................6

3.3.2. Status Service ................................................6

3.4. Application Protocol ............................................7

3.5. Conformance Classes .............................................7

4. PRESENTATION LAYER ................................................8

4.1. Syntax Representation ...........................................8

4.2. General Definitions .............................................8

4.3. Reduced Protocol Telegrams ......................................10

4.3.1. Read Telegrams ................................................10

4.3.2. Write Telegrams ...............................................10

4.3.3. Read Status Telegram ..........................................10

4.4. FURTHER TELEGRAMS ...............................................11

4.4.1.  Read data block ..............................................12

4.4.2.  Write data block .............................................12

4.4.3.  Read block addresses .........................................12

4.4.4.  Read block sizes .............................................12

5. SESSION LAYER .....................................................13

5.1. Session Layer Service ...........................................13

5.2. Session Layer Protocol ..........................................13

5.2.1. Description of the used control-characters ....................13

5.2.2. Message transmission ..........................................15

5.2.3. Invocation of response messages ...............................16

5.2.4. Simplex and Half-Duplex Protocol ..............................16

5.3. Conformance Classes .............................................17

6. TRANSMISSION PROTOCOLS ............................................18

6.1. Point to Point connection .......................................18

SAIA - P8  REDUCED PROTOCOL DESCRIPTION                       Page: 3

1.3. Definitions and Abbreviations

-----------------------------

PCD      Programmable Controller generation D of SAIA

OSI      Open System Interface

media    flags,registers,timers,counters,inputs, outputs, real-time

clock, PCD status or display register of a SAIA-PCD

1.4. References

----------

DD-EPFW6-008    The Full P8 protocol description 18/11/93

SAIA - P8  REDUCED PROTOCOL DESCRIPTION                       Page: 4

2. GENERAL DESCRIPTION

-------------------

3. APPLICATION LAYER

-----------------

3.1. Modelling the provided Service

------------------------------

This specification makes use of the terms Client and Server in order to

describe the model of the provided Service by the SAIA-P8 Protocol for the

PCD family.  The Server is defined as the system that behaves externally

as a PCD for a particular service request. The Client is the system that

makes use of the PCD for some particular purpose via a service request.

The Client may be another PCD or any other system which can drive the

protocol (adapted from ISO 9506/1).

SAIA-PCD or other computer            SAIA-PCD

�������������������Ŀ             ������������������������������������Ŀ

� Client (active)   �             � Server (passive)                   �

�   ���������������Ĵ             ���������������Ŀ   ��������������Ŀ �

�   � Requesting    �             � Responding    �   � the medias   � �

�   �   �����������Ĵ  Request    �����������Ŀ   �   � and programs � �

�   �   � Sending   �����������>�Ĵ Receiving �������>� of the       � �

�   �   �����������Ĵ             �������������   �   � SAIA PCD     � �

�   �   �����������Ĵ  Response   �����������Ŀ   �   �              � �

�   �   � Receiving ��<����������Ĵ Sending   �<�����Ĵ              � �

�   �   �����������Ĵ             �������������   �   �              � �

�   ���������������Ĵ             �����������������   ���������������� �

���������������������             ��������������������������������������

3.2. Formats of the Medias

---------------------

3.2.1. Binary Format

-------------

Binary values are represented by one Bit 0 or 1. For the transmission they

may be coded as the ASCII characters '0' and '1'.

3.2.2. Integer Format

--------------

The integer format is based on 32 Bits with the following format:

�               �               �               �               �

���������������������������������������������������������������Ŀ

�s�x�x�x�x�x�x�x�x�x�x�x�x�x�x�x�x�x�x�x�x�x�x�x�x�x�x�x�x�x�x�x�

�����������������������������������������������������������������

31                                                             0

where     x - 31 bit value

s - sign

The sign bit is a zero for a positive value, and a one for a negative

value.

SAIA - P8  REDUCED PROTOCOL DESCRIPTION                       Page: 5

The range allowed by this format is as follows:

DECIMAL

2'147'483'647       >   VALUE    >  -2'147'483'648

BINARY (HEXADECIMAL)

7FFF'FFFF            >   VALUE    >   8000'0000

3.2.3. Floating-Point Format

---------------------

The floating point format is based on 32 Bits with the following format:

�               �               �               �               �

���������������������������������������������������������������Ŀ

�m�m�m�m�m�m�m�m�m�m�m�m�m�m�m�m�m�m�m�m�m�m�m�m�s�e�e�e�e�e�e�e�

�����������������������������������������������������������������

31                                                             0

where   m  - 24-bit mantissa

s  - sign of the number

e  - 7-bit exponent in excess 64 notation

The mantissa is considered to be a binary fixed point fraction and except

for zero it is always normalized (has a one bit in its highest position).

Thus, it represents a value of less than one but greater than or equal to

one-half.

The sign bit is a zero for a positive value, and a one for a negative

value.

The exponent is the power of two needed to correctly position the mantissa

to reflect the number's true arithmetic value. It is held in excess 64

notation which means that the two's complement values are adjusted upward

by 64, thus changing 40H (-64) through 3FH (+63) to 00H through 7FH. This

facilitates comparisions among floating-point values.

The value of zero is defined as all 32 bits being zeroes. The sign,

exponent, and mantissa are entirely cleared. Thus, zeroes are always

treated as positive.

The range allowed by this format is as follows:

DECIMAL                18                                 -20

9.22337177 * 10    >  +VALUE    >  5.42101070 * 10

18                                 -20

-9.22337177 * 10    >  -VALUE    > -2.71050535 * 10

BINARY (HEXADECIMAL)

63                                   -63

.FFFFFF  *  2       >  +VALUE    >   .FFFFFF  *  2

63                                   -63

-.FFFFFF  *  2       >  -VALUE    >  -.FFFFFF  *  2

SAIA - P8  REDUCED PROTOCOL DESCRIPTION                       Page: 6

3.3. Application Service

-------------------

For the exact definitions of the Instructions used by the PCD to use

this service, please see the PCD Reference Manual.

3.3.1. Variable Access Service

-----------------------

Each variable has a certain Type.  The following Types are defined for

the PCD:

�����������������������������������������������������������Ŀ

�  code: � type:                 � formats:                 �

�����������������������������������������������������������Ĵ

�  R     � register              � integer / floating point �

�  C     � counter               � positiv integer          �

�  T     � timer                 � positiv integer          �

�  F     � flag                  � binary                   �

�  I     � input                 � binary                   �

�  O     � output                � binary                   �

�  K     � the real time clock   � special format           �

�  D     � the display register  � any format               �

�������������������������������������������������������������

On these variables the Read Service and the Write Service is defined,

one may read or write these variables.  The variables are accessed by

its logical nummeric address (direct addressing).

3.3.2. Status Service

--------------

The status of the PCD may be requested by the Client.  The following

states are defined for each Prozessor in the PCD:

S       Stopped (by the debugger)

H       Halted  (by different reasons)

R       Running

C       Conditional running (by the debugger, waiting for

breakpoints)

D       Disconnected (this Prozessor is not in the PCD)

SAIA - P8  REDUCED PROTOCOL DESCRIPTION                       Page: 7

3.4. Application Protocol

--------------------

Two different protocol procedures between a Client and a Server are used.

<write-request>  -> does not ask any response

<read-request>   -> asks a <read-response>

Write & control procedure:

-------------------------

CLIENT                                            SERVER

�                                                �

�-------------<write request>------------------->� write or control

�                                                � action

Read procedure:

--------------

CLIENT                                           SERVER

�                                                �

�-------------<read request>-------------------->� read action

�                                                �

�                                                �

�<------------<read response>--------------------�

�                                                �

3.5. Conformance Classes

-------------------

There are two classes of application services defined.

�����������������������������������������������������Ŀ

�  Class                 � included Services          �

�����������������������������������������������������Ĵ

�  reduced P8 Protocol   � Variable Service           �

�  MD/SD mode            � State Service              �

�����������������������������������������������������Ĵ

�  full P8 Protocol      � Further telegrams          �

�������������������������������������������������������

SAIA - P8  REDUCED PROTOCOL DESCRIPTION                       Page: 8

4. PRESENTATION LAYER

------------------

The Presentation Layer ensures that the information is delivered to the

communicating application process in a form that can be used and

understood. While the meaning - semantics - of the information is fully

preserved, the format and language difference - syntax - is defined.

4.1. Syntax Representation

---------------------

+- function and name

|

v

read input, output, flag

01 cmd ::=      'R' ('I' | 'O' | 'F') <count> <address-IOF>

sts ::=      {<bit-value>}+

^  ^ ^

|  | |

|  | +--sts status telegram from the SERVER to the CLIENT

|  |     the <read response> entity

|  |

|  +--cmd command telegram from the CLIENT to the SERVER

|      the <request> entity

|

+---command code for the telegram (internal registration)

{ <a> }+  represents :

- for read   (<count>+1) occurrences of the expression <a>

- for write  ( 1 to 16 ) occurrences of the expression <a>

- for read/write user memory

(<length+1>)  occurrences of the expression <a>

length max. = 1F hex

[ <a> ]   represents an optional parameter

4.2. General Definitions

-------------------

<break-point>   ::= 'S' <status> <mask> |

'D' <operator> <8-hex-digit> |

'N' <operator> <4-hex-digit> |

('I' | 'O' | 'F' ) <address-IOF> <bit-value>|

'P' <operator> <address-prog> |

'E' <op-code> |

('R' | 'T' | 'C' ) <address-RTC> <operator>

<8-hex-digit> |

'B' <8-hex-digit>

'L' <op-code><operand>

(arithmetic Status, Display register, Input, Output, Flag,instruction

SAIA - P8  REDUCED PROTOCOL DESCRIPTION                       Page: 9

Pointer, op-codE, Register, Timer, Counter, numBer of steps,

iNdex register, instruction Line)

<count>         ::= <hex-digit>       ; value 0 means 1 count !

<address-IOF>   ::= <4-hex-digit>

<address-RTC>   ::= <3-hex-digit>

<address-prog>  ::= <6-hex-digit>

<address-68000> ::= <6-hex-digit>

<op-code>       ::= <3-hex-digit>

<operand>       ::= <4-hex-digit>

<text-number>   ::= <3-hex-digit>

<char-position> ::= <4-hex-digit>

<number-of-chars> ::= <4-hex-digit>

<bloc-type>     ::= <hex-digit>

<bloc-number>   ::= <3-hex-digit>

<ascii-char>    ::= <2-hex-digit>

<length>        ::= <2-hex-digit>

<fail-address>  ::= <8-hex-digit>

<nbr_elements>  ::= <4-hex-digit>

<2-hex-digit>   ::= <hex-digit> <hex-digit>

<hex-digit>     ::= '0' | '1' | '2' | '3' | '4' | '5' | '6' | '7' |

'8' | '9' | 'A' | 'B' | 'C' | 'D' | 'E' | 'F'

<fail-text>     ::= <16-character>

<module-type>   ::= <5-character>

<version>       ::= <3-character>

<cpu-number>    ::= <character>

<character>      := printing character code: 20hex -> 7Fhex

<clock-value>   ::= <week-year> <day-week> <year> <month> <day> <hour>

<minute> <second>

<fail-date>     ::= <year> <month> <day> <hour> <minute> <second>

<week-year>     ::= <dec-digit> <dec-digit>

<day-week>      ::= <dec-digit> <dec-digit>

<year>          ::= <dec-digit> <dec-digit>

<month>         ::= <dec-digit> <dec-digit>

<day>           ::= <dec-digit> <dec-digit>

<hour>          ::= <dec-digit> <dec-digit>

<minute>        ::= <dec-digit> <dec-digit>

<second>        ::= <dec-digit> <dec-digit>

<dec-digit>     ::= '0' | '1' | '2' | '3' | '4' | '5' | '6' | '7' |

'8' | '9'

<status>        ::= <flags>

<mask>  #�        ::= <flags>

<flags>         ::= <zero-flag> <neg-flag> <error-flag> <accu-flag>

<zero-flag>     ::= <bit-value>

<neg-flag>      ::= <bit-value>

<error-flag>    ::= <bit-value>

<accu-flag>     ::= <bit-value>

<bit-value>     ::= '0' | '1'

<operator>      ::= '<' | '=' | '>' | '#'

'#' means  not equal

<sblock>        ::= <2-hex-digit>

<act_trans>     ::= <4-hex-digit>[<act_trans>]

SAIA - P8  REDUCED PROTOCOL DESCRIPTION                       Page: 10

4.3. Reduced Protocol Telegrams

--------------------------

4.3.1. Read Telegrams

--------------

read input, output, fla

00 cmd ::=      'R' ('I' | 'O' | 'F') <count> <address-IOF>

sts ::=      {<bit-value>}+

read register, timer, counter

01 cmd  ::=     'R' ('R' | 'T' | 'C') <count> <address-RTC>

sts  ::=     {<8-hex-digit>}+

read real time clock

07 cmd  ::=     'RK'

sts  ::=     <clock-value>

read display register

10 cmd  ::=     'RD'

sts  ::=     <8-hex-digit>

4.3.2. Write Telegrams

---------------

write output, flag

20 cmd  ::=     'W' ('O' | 'F') <address-IOF> {<bit-value>}+

sts  ::=     empty

write register, timer, counter

21 cmd  ::=     'W' ('R' | 'T' | 'C') <address-RTC> {<8-hex-digit>}+

sts  ::=     empty

write real time clock

27 cmd  ::=     'WK' <clock-value>

sts  ::=     empty

4.3.3. Read Status Telegram

--------------------

read PCD status

11 cmd  ::=     'RS' ( '0' | '1' | ... | '6' | '7' )

0->6 cpu number ;   7 own

sts  ::=     'S' | 'H' | 'R' | 'C' | 'D'

SAIA - P8  REDUCED PROTOCOL DESCRIPTION                       Page: 11

4.4. FURTHER TELEGRAMS

-----------------

The following telegrams CANNOT be accessed from MD/SD mode, however

the SAIA LIBRARY routines allow access to them under the following

conditions :-

PCD4/PCD6.M540/PCD2 : The PGU port and the K111 cable are used.

PCD6                : The P800 is used

Definitions

-----------

<count>         1 hex digit: 0..F (0=1 item, F=16 items)

<bloc-type>     2 hex digits: 07=DB

<block-number>  4 hex digits (0000H..FFFFH)

<db-number>     4 hex digits (0000H..1F3FH)

<db-element>    4 hex digits (0000H..3FFFH)

NOTES:

1)  The existing <bloc-number> is only 3 hex digits (0..4095),

the new <block-number> is 4 hex digits (0..65535).

2)  The existing <text-number> is only 3 hex digits (0..4095),

the new <txt-number> is 4 hex digits (0..65535).

3)  The existing <bloc-type> has a value 7 for data blocks (DB).

4)  When writing the firmware for the new data memory, take into

account that the "type" indicator byte may be extended later,

and may not always be 8 (text) or 32 (data block).

5)  The read/write text and data block telegrams may attempt to

access characters or elements beyond the end of the text/DB.

For texts/DBs 0..3999, the length can only be determined by

reading it all until the NUL terminator is found. This is

slow, therefore NO checks should be done by the firmware to

detect access beyond the end of a text/DB (this is how it is

with the existing firmware). It is the responsibility of the

application program (PG1/PG3) to determine the length first,

using the "read block size" telegram.

For texts/DBs 4000..7999, the length is known, therefore

telegrams which would access beyond the end must return a

NAK immediately.

SAIA - P8  REDUCED PROTOCOL DESCRIPTION                       Page: 12

4.4.1.  Read data block

----------------

Works for data blocks 0..3999 in text memory (stored in encoded

binary format), and for data blocks 4000..7999 in the new data

memory. Returns NAK if the DB doesn't exist or it's not a DB

(0..3999: if 1st byte is not FFH, 4000..7999: if "type" is not

32).

cmd := 'RZ' <count> <db-number> <db-element>

sts := {<8-hex-digit>}+

4.4.2.  Write data block

-----------------

Works for data blocks 0..3999 in text memory (stored in encoded

binray format), and for data blocks 4000..7999 in the new data

memory. Returns NAK if the DB doesn't exist or is not a DB

(0..3999: if 1st byte is not FFH, 4000..7999: if "type" is not 32).

cmd := 'WZ' <db-number> <db-element> {<8-hex-digit>}+

4.4.3.  Read block addresses

---------------------

Returns the user-memory address of the start of a given block,

text or data block, and up to 16 consecutive blocks. Returns

<address-prog> = 0 if the block doesn't exist, or 0xFFFFFF if

a text address is requested and the block is in use as a DB

or vice-versa. Works for texts and data blocks in the existing

text memory, as well as in the new data memory. The address is

the long word offset from the start of user memory, min 100

(NOT the start of the CPU's memory).

cmd := 'R1' <count> <bloc-type> <block-number>

sts := {<address-prog>}+

4.4.4.  Read block sizes

-----------------

Returns the size of a one or more code blocks in program lines,

texts in characters, or data blocks in elements.

Returns a size of 0 if the item doesn't exist, or 0xFFFFFF if

a text size is requested and the block is in use as a DB or

vice-versa.

cmd := 'R2' <count> <bloc-type> <block-number>

sts := {<6-hex-digits>}+

read system program version

14 cmd  ::=     'RV'

sts  ::=     <module-type> <version> <cpu-number>

SAIA - P8  REDUCED PROTOCOL DESCRIPTION                       Page: 13

5. SESSION LAYER

-------------

5.1. Session Layer Service

---------------------

The Session Layer provides the means for the cooperating systems to

organize and synchronize their dialog and manage their data exchange.

The session layer ensures that all information is received at the

destination and does not get lost.

The Session Layer provides for interaction management of the end to end

communication, the management of whose turn it is to send is handled -

simplex or half duplex.

Through the use of a synchronisation procedure, the Session Layer can

identify and recover from errors in the data flow.  It can also report

to the application abnormal situations that have not been corrected.

Two Session Layer Services are defined:

- The controlled transmission of a message

- The controlled invocation of a response message

5.2. Session Layer Protocol

----------------------

The Session Layer for the P8 - Protocol is based on DIN 66019.  This is

an character oriented not transparent (code dependent) point to point

protocol.  It may be used on synchronous or asynchronous transmissions.

Note: DIN 66019 is normaly considered to be a Link Layer Protocol.

However in this context it is used as an end-to-end protocol to control

the dialog, what is exactly the Session Layer Function.

5.2.1. Description of the used control-characters

------------------------------------------

All characters use only 7 bits.  The transmitted telegrams from the

presentation layer are not allowed to contain any of the following

control characters.

STX      Start of TeXt  (^B)

A character delimiting that part of a message which

constitutes the telegram.

Note:  - is not included in the block checksum

ETX      End of TeXt    (^C)

A control character used to delimit the end of a series of

characters constituting the telegram of a message.

Note:  - requests a reply ACK or NAK

- starts the timeout on the sender station

- is followed of the block checksum

- is included in the block checksum

ENQ      ENQuiry   (^E)

A communications control character used to solicit a response

SAIA - P8  REDUCED PROTOCOL DESCRIPTION                       Page: 14

from another station. It is used as the request to send the

values of the previous read request.

Note:  - requests a NAK if the transmit buffer is empty

ACK      ACKnowledgement  (^F)

A control character which represents an affirmative response to

a sender. It acknowledges error-free reception of a block or

segment of a message.

Note:  - cancels the timeout

- frees the transmit buffer

NAK      Negative AcKnowledge (^U)

This character represents a negative response from the receiver

to the sender. It indicates that a block of information has

#�             been received with errors and must be retransmitted.

Note:  - the timeout is reset

- the repeat counter is incremented

- invokes a retransmission of the transmit buffer

EOT      End of Transmission (^D)

This control character is only used if the

messagesynchronisation between the two partners is completely

lost. It clears all buffers and counters and resets the initial

state.

BCC      Block Check Code (any value)

The BCC is a seven bit code. It is the modulo 2 sum of all

characters behind the STX character (excluding the STX

character) and follows immediately the ETX character.

Example:               STX

R       01010010

K       01001011

ETX     00000011

--------

BCC     00011010

SAIA - P8  REDUCED PROTOCOL DESCRIPTION                       Page: 15

5.2.2. Message transmission

--------------------

Each message is acknowledged by the receiving part.  The acknowledge

means, that the corresponding action is already performed.  The sending

part clears the transmission buffer only after the reception of the ACK

and sends the next message.

Sending                                           Receiving

�                                                �

�----------STX<cmd>ETX BCC---------------------->�

�                                                � action

�<---------ACK-----------------------------------�

�                                                �

�----------STX<cmd>ETX BCC---->   next message invokes next action

�

On a transmission error the receiving part replies with a NAK and the

sending part sends again the contens of the transmit buffer.  This

mechanisme is repeated 3 times.  Afterwards the session layer informs

the upper layers about the failure in the transmission connection.

Sending                                           Receiving

�                                                �

�----------STX<cmd>ETX BCC---------------------->� BCC error

�                                                � detection

�<---------NAK-----------------------------------�

�                                                �

�----------STX<cmd>ETX BCC---------------------->� BCC correct

�                                                �

�<---------ACK-----------------------------------� action

�                                                �

If a message is not acknowledged after 3 seconds it is repeated. A

message is repeated only 3 times.

�----------STX<cmd>ETX BCC------------>?????     �

3s �                                                �

�----------STX<cmd>ETX BCC---------------------->�

�                                                � action

3s �  ???<----ACK-----------------------------------�

�                                                �

�----------STX<cmd>ETX BCC---------------------->� repeat

�                                                � action

�<---------ACK-----------------------------------�

�                                                �

Note: The actions in the reduced SAIA-P8  protocol are defined that a

way, that they can be repeated without any problems.

SAIA - P8  REDUCED PROTOCOL DESCRIPTION                       Page: 16

5.2.3. Invocation of response messages

-------------------------------

A Server is not allowed to send any <read-response> telegrams to the

Client without any prior enquiry (ENQ) command.  This mechansime allows

the Client to prepare his internal receive buffer to receive the

telegram.

CLIENT                                           SERVER

�                                                �

�----------STX<cmd>ETX BCC---------------------->� action and

�                                                � preparation of

�<---------ACK-----------------------------------� response (read

�                                                � value)

�                                                �

�----------ENQ---------------------------------->�

�                                                � just creat the

�<---------STX<sts>ETX BCC-----------------------� response and send

�                                                � it.

�----------ACK---------------------------------->� clears the

�                                                � transmitbuffer

Remark:  A NAK reply to the <read-response> just repeats the

transmission of the transmit buffer contens.  The repetition of the ENQ

creats anothertime the response message.  However on a <read-request> to

read a variable, the value of the variable is only read on the action

befor the ACK is returned.

5.2.4. Simplex and Half-Duplex Protocol

--------------------------------

If both stations are Client and Server in the same time a half duplex

protocol is used.  In the half duplex operation ENQ, ACK or NAK characters

may be inserted in a datagram in the other direction.  The two stations

must be able to detect these characters inside the messages.  A second

message is only sended, if the previous message is acknowledged with ACK

or the timeout of 3 seconds is reached.  To avoid deadlock conditions, one

station in a half duplex configuration (both stations Client and Server)

is the Master and the otherone the Slave.  In case of conflict, the

Master-Client has priority over the Slave-Client.

In a simplex operation one station is the Client and the otherone the

Server.  As the transmitbuffer of the Server is only used for

<read-response>, the Client does not need to acknowledge the

<read-response>, it just passes the next request.

To get full upward compatibility from the simplex to the half duplex

operation, the <read-response> message is never repeated after a timeout

by a Server.  The Client is free to ask a repetition of a wrong received

<read-response> with a NAK within 3 seconds (retransmits the contens of

the transmit buffer) or ENQ after 3 seconds (retransmits the response to

the last request).

SAIA - P8  REDUCED PROTOCOL DESCRIPTION                       Page: 17

5.3. Conformance Classes

-------------------

The Station with Client and Server must implement the half duplex

Session Protocol and stations with only Server or only Client may

implement the more simpler simplex protocol.

SAIA - P8  REDUCED PROTOCOL DESCRIPTION                       Page: 18

6. TRANSMISSION PROTOCOLS

----------------------

6.1. Point to Point connection

-------------------------

The asynchronous connection has the following parameters:

- speed in bit per second (bps)

- number of bits per character ( 6,7 or 8)

- parity Even / Odd / fix High / fix Low / No parity

- number of stop bits (one or two)

Example:

short form:  9600,7,E,1

meaning   :  speed 9600 bps , 7 bits/character, Even parity,

one stop bit

See the PCD hardware manuals for the pin assignement and data of the

communication interfaces.

Note: There exist an additional protocol on the control lines for the PGU

----  class of interface.

RTS   Request to send

This signal is sended by the Client to ask the Server if he is ready to

receive a message.

CTS   Ready to sending

This signal is used by the Server to reply to the RTS that it is ready to

receive a message.

Telegrams received without correct control lines on the PGU class are

refused with NAK.